## Info
Abbreviation | Description
AC | Alternating current or AC-coupled
BAT | Battery
c | compulsory information
DC | Direct current or DC-coupled
EG | Efficiency guideline (German Effizienzleitfaden)
max | maximum
min | minimum
MPP | Maximum Power Point
nom | nominal
ns | not specified
o | optional information
PE | Power electronics
PerMod | Performance Simulation Model for PV-Battery Systems
PVINV | PV-inverter
PV | Photovoltaics or PV-coupled

## Data
|  |  | EG abbreviations | PerMod abbreviations | Unit |  | Exemplary systems |  |  |  | PV-inverter | PV-inverter |  | Templates
| Abbreviations (see also work sheet 'Info'): |  |  | Number |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | End
| c | compulsory information |  | ID |  | SG1 | S2 | S3 | S4 | S5 | INV1 | INV2
| ns | not specified |  | Man1 | Manufacturer 1 | Generic | Siemens | KOSTAL | KOSTAL | Fronius | SMA | SMA |  | A | B | C | D
| o | optional information |  | Pro1 | Product 1 | AC-System | Junelight Smart Battery 9,9 | PLENTICORE plus 5.5 | PLENTICORE plus 10 | Symo GEN24 10.0 Plus | Sunny Boy 5.0 | Sunny Tripower 10.0 |  | AC | DC | PV | PVINV
|  |  |  | Man2 | Manufacturer 2 | 3 S3: BYD; 4 S4: BYD; 5 S5: BYD |  | PE+BAT | PE+BAT | PE+BAT | PE
|  |  |  | Pro2 | Product 2 | 3 S3: Battery-Box H6.4; 4 S4: Battery-Box H11.5; 5 S5: Battery-Box H11.5
|  |  |  | Man3 | Manufacturer 3
|  |  |  | Pro3 | Product 3
|  |  |  | Info | Info
|  |  |  | Cat | Category | A | A | B | B | B | D | D |  | A | B | C | D
|  |  |  | Top | Topology | AC | AC | DC | DC | DC | PVINV | PVINV |  | AC | DC | PV | PVINV
|  |  |  | Type | Type | PE+Bat | PE+BAT | PE+BAT | PE+BAT | PE+BAT | PE | PE |  | PE+BAT | PE+BAT | PE+BAT | PE
PV connection | bar: 2 S2 to 7 INV2
| Rated PV input power (DC) |  | P_PV,nom | P_PV2AC_in | W | o | o | 5686 | 10380 | 10222.5 | 4764.1676 | 10214.5046 |  | o | c | c | c
| Rated PV output power (AC) |  | P_PV-INV,nom | P_PV2AC_out | W | o | o | ns | ns | ns | 4600 | 10000 |  | o | ns | o | c
PV input voltage
|  | Minimum | U_PV,min | U_PV_min | V | o | o | 120 | 120 | 80 | 100 | 125 |  | o | c | c | c
|  | Nominal | U_PV,nom | U_PV_nom | V | o | o | 570 | 570 | 610 | 400 | 580 |  | o | c | c | c
|  | Maximum | U_PV,max | U_PV_max | V | o | o | 1000 | 1000 | 1000 | 600 | 1000 |  | o | c | c | c
Maximum Power Point (MPP) voltage
|  | Minimum | U_MPP,min | U_MPP_min | V | o | o | 225 | 405 | 278 | 175 | 320 |  | o | c | o | c
|  | Maximum | U_MPP,max | U_MPP_max | V | o | o | 720 | 720 | 800 | 500 | 800 |  | o | c | o | c
AC connection
| Rated PV output power (AC) |  | P_AC,nom (export) | P_PV2AC_out | W | ns | ns | 5487 | 9921 | 10042.4 | ns | ns |  | ns | c | o | ns
| Rated input power (AC) |  | P_AC,nom (import) | P_AC2BAT_in | W | ns | ns | o | o | 9997.2 | ns | ns |  | ns | o | ns | ns
| Nominal charging power (AC) |  | P_BESS,nom (charging) | P_AC2BAT_in | W | 1000 | 3572 | ns | ns | ns | ns | ns |  | c | ns | ns | ns
| Nominal discharging power (AC) |  | P_BESS,nom (discharging) | P_BAT2AC_out | W | 1000 | 3507 | ns | ns | ns | ns | ns |  | c | ns | ns | ns
| Nominal discharging power (AC) |  | P_AC,nom (discharging) | P_BAT2AC_out | W | ns | ns | 3157 | 5776 | 9822.6 | ns | ns |  | ns | c | o | ns
DC connection
| Nominal charging power of the battery converter (input) |  | P_BESS,nom (charging) | P_PV2BAT_in | W | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
| Nominal discharging power of the battery converter (output) |  | P_BESS,nom (discharging) | P_BAT2PV_out | W | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
Battery connection
| Nominal charging power (DC) |  | P_BAT,nom (charging) | P_PV2BAT_out | W | 950 | 3391.8 | 3445 | 6214 | 9723.6 | ns | ns |  | c | c | c | ns
| Nominal discharging power (DC) |  | P_BAT,nom (discharging) | P_BAT2AC_in | W | 1053 | 3719 | 3319 | 6008 | 10060.2 | ns | ns |  | c | c | c | ns
Battery
Battery voltage
|  | Minimum | U_BAT,min | U_BAT_min | V | ns | 42 | 200 | 360 | 360 | ns | ns |  | c | c | c | ns
|  | Nominal | U_BAT,nom | U_BAT_nom | V | ns | 51.8 | 256 | 460 | 460 | ns | ns |  | c | c | c | ns
|  | Maximum | U_BAT,max | U_BAT_max | V | ns | 58.8 | 282 | 500 | 500 | ns | ns |  | c | c | c | ns
Usable battery capacity
|  | 100% of nominal power | E_BAT,use (100%) | E_BAT_100 | kWh | 1 | 8.885 | 5.757 | 10.612 | 9.6919 | ns | ns |  | o | o | o | ns
|  | 50% of nominal power | E_BAT,use (50%) | E_BAT_50 | kWh | 1 | 8.867 | 5.606 | 10.441 | 9.62 | ns | ns |  | o | o | o | ns
|  | 25% of nominal power | E_BAT,use (25%) | E_BAT_25 | kWh | 1 | 8.787 | 5.68 | 10.468 | 9.8253 | ns | ns |  | o | o | o | ns
|  | Mean | E_BAT,use | E_BAT_usable | kWh | 1 | 8.8463 | 5.681 | 10.507 | c | ns | ns |  | c | c | c | ns
Battery efficiency
|  | 100% of nominal power | eta_BAT,RTE (100%) | eta_BAT_100 | % | 94 | 96.4 | 95.08 | 95.39 | 95.9252 | ns | ns |  | o | o | o | ns
|  | 50% of nominal power | eta_BAT,RTE (50%) | eta_BAT_50 | % | 95 | 97.2 | 95.2 | 95.48 | 96.4972 | ns | ns |  | o | o | o | ns
|  | 25% of nominal power | eta_BAT,RTE (25%) | eta_BAT_25 | % | 96 | 97 | 94.17 | 94.98 | 95.9858 | ns | ns |  | o | o | o | ns
|  | Mean | eta_BAT,RTE | eta_BAT | % | 95 | 96.8667 | 94.8167 | 95.2833 | c | ns | ns |  | c | c | c | ns
Standby losses
Standby power consumption in fully charged state
|  | AC power demand | P_Standby,AC (SOC_MAX) | P_SYS_SOC1_AC | W | 5 | 14.9 | ns | ns | ns | ns | ns |  | c | ns | ns | ns
|  | DC power demand | P_Standby,DC (SOC_MAX) | P_SYS_SOC1_DC | W | 0.02 | 0.1 | 0.15 | 0.15 | 44 | ns | ns |  | c | c | c | ns
Standby power consumption in fully discharged state
|  | AC power demand | P_Standby,AC (SOC_MIN) | P_SYS_SOC0_AC | W | 10 | 12.1 | 4.47 | 4.47 | 9 | ns | ns |  | c | c | c | ns
|  | DC power demand | P_Standby,DC (SOC_MIN) | P_SYS_SOC0_DC | W | 0 | 0 | 4.56 | 4.71 | 0 | ns | ns |  | c | c | c | ns
Power consumption of other system components
| Standby power consumption of the PV inverter | AC power demand | P_PV-INV,Standby,AC | P_PVINV_AC | W | o | o | ns | ns | ns | 1 | 5 |  | o | ns | o | c
| Power consumption of other system components | AC power demand | P_PERIPH,AC | P_PERI_AC | W | 2 | 1 | 1.55 | 1.77 | 1 | ns | ns |  | c | c | c | ns
Control properties
| Mean stationary deviation of the charging power (import) |  | P_GRID (import,charging) | P_PV2BAT_DEV_IMPORT | W | 0 | 0.6 | 0 | 1.34 | 1 | ns | ns |  | c | c | c | ns
| Mean stationary deviation of the charging power (export) |  | P_GRID (export,charging) | P_PV2BAT_DEV_EXPORT | W | 0 | 2.1 | 13.84 | 10.97 | 2.9 | ns | ns |  | c | c | c | ns
| Mean stationary deviation of the discharging power (import) |  | P_GRID (import,discharging) | P_BAT2AC_DEV_IMPORT | W | 0 | 1.9 | 1.98 | 2.98 | 3 | ns | ns |  | c | c | c | ns
| Mean stationary deviation of the discharging power (export) |  | P_GRID (export,discharging) | P_BAT2AC_DEV_EXPORT | W | 0 | 0.8 | 2.86 | 2.65 | 1.2 | ns | ns |  | c | c | c | ns
| Mean dead time |  | t_T | t_DEAD | s | 0 | 1.6 | 0.63 | 0.61 | 1.6 | ns | ns |  | c | c | c | ns
| Mean settling time |  | t_E | t_SETTLING | s | 0 | 3.8 | 2.79 | 2.74 | 14.2 | ns | ns |  | c | c | c | ns
Efficiencies of the energy conversion pathways at nominal PV input voltage
| PV2AC sampling points (exact output power/nominal output power) | Output power/nominal output power
|  | 0.05 |  | p_PV2AC_5 |  | o | o | 0.043922 | 0.047 | 0.046682 | c | 0.05 |  | o | c | o | c
|  | 0.1 |  | p_PV2AC_10 |  | o | o | 0.095298 | 0.099 | 0.094619 | 0.1087 | 0.1 |  | o | c | o | c
|  | 0.2 |  | p_PV2AC_20 |  | o | o | 0.19718 | 0.201 | 0.19791 | c | 0.2 |  | o | c | o | c
|  | 0.25 |  | p_PV2AC_25 |  | o | o | 0.24764 | 0.252 | 0.24537 | 0.27174 | 0.25 |  | o | c | o | c
|  | 0.3 |  | p_PV2AC_30 |  | o | o | 0.29769 | 0.303 | 0.3009 | c | 0.3 |  | o | c | o | c
|  | 0.5 |  | p_PV2AC_50 |  | o | o | 0.50009 | 0.506 | 0.49835 | 0.54348 | 0.5 |  | o | c | o | c
|  | 0.75 |  | p_PV2AC_75 |  | o | o | 0.75068 | 0.755 | 0.74947 | 0.81522 | 0.75 |  | o | c | o | c
|  | 1 |  | p_PV2AC_100 | [9 empty] | o | c | o | c | bar: 1 SG1 to 7 INV2
| PV2AC efficiencies | Output power/nominal output power
|  | 0.05 | eta_PV2AC,t (5%) | eta_PV2AC_5 | % | o | o | 86.94 | 91.03 | 93.7937 | c | 94.4 |  | o | c | o | c
|  | 0.1 | eta_PV2AC,t (10%) | eta_PV2AC_10 | % | o | o | 92.72 | 94.8 | 96.397 | 95.41 | 96.6 |  | o | c | o | c
|  | 0.2 | eta_PV2AC,t (20%) | eta_PV2AC_20 | % | o | o | 95.34 | 96.31 | 97.6461 | c | 97.8 |  | o | c | o | c
|  | 0.25 | eta_PV2AC,t (25%) | eta_PV2AC_25 | % | o | o | 95.84 | 96.52 | 97.8979 | 96.8 | 98.1 |  | o | c | o | c
|  | 0.3 | eta_PV2AC,t (30%) | eta_PV2AC_30 | % | o | o | 96.11 | 96.65 | 97.9923 | c | 98.2 |  | o | c | o | c
|  | 0.5 | eta_PV2AC,t (50%) | eta_PV2AC_50 | % | o | o | 96.6 | 96.71 | 98.0849 | 97.11 | 98.3 |  | o | c | o | c
|  | 0.75 | eta_PV2AC,t (75%) | eta_PV2AC_75 | % | o | o | 96.63 | 96.21 | 98.0355 | 96.79 | 98.2 |  | o | c | o | c
|  | 1 | eta_PV2AC,t (100%) | eta_PV2AC_100 | % | o | o | 96.5 | 95.56 | 97.897 | 96.5541 | 97.9 |  | o | c | o | c
| PV2BAT sampling points (exact output power/nominal output power) | Output power/nominal output power
|  | 0.05 |  | p_PV2BAT_5 |  | ns | ns | 0.03 | 0.04 | 0.043821 | ns | ns |  | ns | c | c | ns
|  | 0.1 |  | p_PV2BAT_10 |  | ns | ns | 0.08 | 0.09 | 0.091962 | ns | ns |  | ns | c | c | ns
|  | 0.2 |  | p_PV2BAT_20 |  | ns | ns | 0.19 | 0.19 | 0.19478 | ns | ns |  | ns | c | c | ns
|  | 0.25 |  | p_PV2BAT_25 |  | ns | ns | 0.24 | 0.24 | 0.24277 | ns | ns |  | ns | c | c | ns
|  | 0.3 |  | p_PV2BAT_30 |  | ns | ns | 0.29 | 0.29 | 0.29831 | ns | ns |  | ns | c | c | ns
|  | 0.5 |  | p_PV2BAT_50 |  | ns | ns | 0.49 | 0.5 | 0.4972 | ns | ns |  | ns | c | c | ns
|  | 0.75 |  | p_PV2BAT_75 |  | ns | ns | 0.75 | 0.75 | 0.75114 | ns | ns |  | ns | c | c | ns
|  | 1 |  | p_PV2BAT_100 | [9 empty] | ns | c | c | ns | bar: 1 SG1 to 7 INV2
| PV2BAT efficiencies | Output power/nominal output power
|  | 0.05 | eta_PV2BAT,t (5%) | eta_PV2BAT_5 | % | ns | ns | 73.65 | 83.83 | 93.3232 | ns | ns |  | ns | c | c | ns
|  | 0.1 | eta_PV2BAT,t (10%) | eta_PV2BAT_10 | % | ns | ns | 85.82 | 91.34 | 96.6501 | ns | ns |  | ns | c | c | ns
|  | 0.2 | eta_PV2BAT,t (20%) | eta_PV2BAT_20 | % | ns | ns | 91.71 | 94.78 | 97.8713 | ns | ns |  | ns | c | c | ns
|  | 0.25 | eta_PV2BAT,t (25%) | eta_PV2BAT_25 | % | ns | ns | 92.85 | 95.57 | 98.2072 | ns | ns |  | ns | c | c | ns
|  | 0.3 | eta_PV2BAT,t (30%) | eta_PV2BAT_30 | % | ns | ns | 93.55 | 96.04 | 98.4825 | ns | ns |  | ns | c | c | ns
|  | 0.5 | eta_PV2BAT,t (50%) | eta_PV2BAT_50 | % | ns | ns | 95.06 | 96.95 | 98.9117 | ns | ns |  | ns | c | c | ns
|  | 0.75 | eta_PV2BAT,t (75%) | eta_PV2BAT_75 | % | ns | ns | 95.71 | 97.34 | 99.0776 | ns | ns |  | ns | c | c | ns
|  | 1 | eta_PV2BAT,t (100%) | eta_PV2BAT_100 | % | ns | ns | 96.07 | 97.36 | 99.0701 | ns | ns |  | ns | c | c | ns
| AC2BAT sampling points (exact output power/nominal output power) | Output power/nominal output power
|  | 0.05 |  | p_AC2BAT_5 |  | 0.047717 | 0.028716 | o | o | 0.047717 | ns | ns |  | c | o | ns | ns
|  | 0.1 |  | p_AC2BAT_10 |  | 0.098327 | 0.078808 | o | o | 0.098327 | ns | ns |  | c | o | ns | ns
|  | 0.2 |  | p_AC2BAT_20 |  | 0.19857 | 0.18666 | o | o | 0.19857 | ns | ns |  | c | o | ns | ns
|  | 0.25 |  | p_AC2BAT_25 |  | 0.24882 | 0.23684 | o | o | 0.24882 | ns | ns |  | c | o | ns | ns
|  | 0.3 |  | p_AC2BAT_30 |  | 0.29891 | 0.29462 | o | o | 0.29891 | ns | ns |  | c | o | ns | ns
|  | 0.5 |  | p_AC2BAT_50 |  | 0.49854 | 0.4987 | o | o | 0.49854 | ns | ns |  | c | o | ns | ns
|  | 0.75 |  | p_AC2BAT_75 |  | 0.74641 | 0.75464 | o | o | 0.74641 | ns | ns |  | c | o | ns | ns
|  | 1 |  | p_AC2BAT_100 |  | 1 | 1 | o | o | 1 | ns | ns |  | c | o | ns | ns
| AC2BAT efficiencies | Output power/nominal output power
|  | 0.05 | eta_AC2BAT (5%) | eta_AC2BAT_5 | % | 70 | 72.9 | o | o | 93.3159 | ns | ns |  | c | o | ns | ns
|  | 0.1 | eta_AC2BAT (10%) | eta_AC2BAT_10 | % | 85 | 87.1 | o | o | 95.8455 | ns | ns |  | c | o | ns | ns
|  | 0.2 | eta_AC2BAT (20%) | eta_AC2BAT_20 | % | 90 | 92.9 | o | o | 96.8954 | ns | ns |  | c | o | ns | ns
|  | 0.25 | eta_AC2BAT (25%) | eta_AC2BAT_25 | % | 92 | 94.1 | o | o | 97.1618 | ns | ns |  | c | o | ns | ns
|  | 0.3 | eta_AC2BAT (30%) | eta_AC2BAT_30 | % | 94 | 94.7 | o | o | 97.2404 | ns | ns |  | c | o | ns | ns
|  | 0.5 | eta_AC2BAT (50%) | eta_AC2BAT_50 | % | 95 | 95.6 | o | o | 97.4425 | ns | ns |  | c | o | ns | ns
|  | 0.75 | eta_AC2BAT (75%) | eta_AC2BAT_75 | % | 95 | 95.4 | o | o | 97.3587 | ns | ns |  | c | o | ns | ns
|  | 1 | eta_AC2BAT (100%) | eta_AC2BAT_100 | % | 95 | 95 | o | o | 97.1622 | ns | ns |  | c | o | ns | ns
| BAT2AC sampling points (exact output power/nominal output power) | Output power/nominal output power
|  | 0.05 |  | p_BAT2AC_5 |  | 0.047717 | 0.052237 | 0.049 | 0.049 | 0.050557 | ns | ns |  | c | c | o | ns
|  | 0.1 |  | p_BAT2AC_10 |  | 0.098327 | 0.10005 | 0.098 | 0.098 | 0.10043 | ns | ns |  | c | c | o | ns
|  | 0.2 |  | p_BAT2AC_20 |  | 0.19857 | 0.1978 | 0.197 | 0.198 | 0.20083 | ns | ns |  | c | c | o | ns
|  | 0.25 |  | p_BAT2AC_25 |  | 0.24882 | 0.24599 | 0.251 | 0.25 | 0.25153 | ns | ns |  | c | c | o | ns
|  | 0.3 |  | p_BAT2AC_30 |  | 0.29891 | 0.29415 | 0.301 | 0.298 | 0.30132 | ns | ns |  | c | c | o | ns
|  | 0.5 |  | p_BAT2AC_50 |  | 0.49854 | 0.49078 | 0.501 | 0.499 | 0.50066 | ns | ns |  | c | c | o | ns
|  | 0.75 |  | p_BAT2AC_75 |  | 0.74641 | 0.75587 | 0.753 | 0.747 | 0.74967 | ns | ns |  | c | c | o | ns
|  | 1 |  | p_BAT2AC_100 | [9 empty] | c | c | o | ns | bar: 1 SG1 to 7 INV2
| BAT2AC efficiencies | Output power/nominal output power
|  | 0.05 | eta_BAT2AC (5%) | eta_BAT2AC_5 | % | 70 | 83.1 | 80.58 | 87.54 | 93.893 | ns | ns |  | c | c | o | ns
|  | 0.1 | eta_BAT2AC (10%) | eta_BAT2AC_10 | % | 85 | 89.3 | 88.15 | 92.44 | 96.2909 | ns | ns |  | c | c | o | ns
|  | 0.2 | eta_BAT2AC (20%) | eta_BAT2AC_20 | % | 90 | 93.4 | 92.3 | 95.02 | 97.278 | ns | ns |  | c | c | o | ns
|  | 0.25 | eta_BAT2AC (25%) | eta_BAT2AC_25 | % | 92 | 94.3 | 93.19 | 95.5 | 97.5482 | ns | ns |  | c | c | o | ns
|  | 0.3 | eta_BAT2AC (30%) | eta_BAT2AC_30 | % | 94 | 94.7 | 93.73 | 95.78 | 97.6863 | ns | ns |  | c | c | o | ns
|  | 0.5 | eta_BAT2AC (50%) | eta_BAT2AC_50 | % | 95 | 95.3 | 94.71 | 96.35 | 97.8667 | ns | ns |  | c | c | o | ns
|  | 0.75 | eta_BAT2AC (75%) | eta_BAT2AC_75 | % | 95 | 95 | 94.93 | 96.27 | 97.8045 | ns | ns |  | c | c | o | ns
|  | 1 | eta_BAT2AC (100%) | eta_BAT2AC_100 | % | 95 | 94.3 | 95.11 | 96.15 | 97.6382 | ns | ns |  | c | c | o | ns
| BAT2PV sampling points (exact output power/nominal output power) | Output power/nominal output power
|  | 0.05 |  | p_BAT2PV_5 | [9 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.1 |  | p_BAT2PV_10 | [9 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.2 |  | p_BAT2PV_20 | [9 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.25 |  | p_BAT2PV_25 | [9 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.3 |  | p_BAT2PV_30 | [9 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.5 |  | p_BAT2PV_50 | [9 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.75 |  | p_BAT2PV_75 | [9 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 1 |  | p_BAT2PV_100 | [9 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
| BAT2PV efficiencies | Output power/nominal output power
|  | 0.05 | eta_BAT2PV (5%) | eta_BAT2PV_5 | % | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.1 | eta_BAT2PV (10%) | eta_BAT2PV_10 | % | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.2 | eta_BAT2PV (20%) | eta_BAT2PV_20 | % | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.25 | eta_BAT2PV (25%) | eta_BAT2PV_25 | % | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.3 | eta_BAT2PV (30%) | eta_BAT2PV_30 | % | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.5 | eta_BAT2PV (50%) | eta_BAT2PV_50 | % | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 0.75 | eta_BAT2PV (75%) | eta_BAT2PV_75 | % | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
|  | 1 | eta_BAT2PV (100%) | eta_BAT2PV_100 | % | [8 empty] | ns | ns | c | ns | bar: 1 SG1 to 7 INV2
Settings for the assessment with the System Performance Index (SPI)
| 1st reference case for SPI (5 kWp) |  |  | ref_1 | yes or no | yes | yes | yes | no | no | ns | ns |  | c | c | c | ns
| 2nd reference case for SPI (10 kWp) |  |  | ref_2 | yes or no | yes | yes | no | yes | yes | ns | ns |  | c | c | c | ns